POLYPROPYLENE PIPE SYSTEMS FOR INFRASTRUCTURAL SEWERAGE PRAGMA TYPE OR SIMILAR

- Application: according the actual “Sewage systems design standards”: thermoplastic pipe system for gravity water drainage of domestic, industrial or rain wastewater.

- Product description – double layer polypropylene pipe with inner smooth layer and trapezoidal profile for the outer layer – type B

- A system of quality control of inputs in construction materials: The pipes are certified by INSTA-CERT and wear the Nordic Poly Mark seal of approval. In connection with the implementation of quality control materials are provided recalls of specimen pipes on a construction site. Seizure of the samples will be carried out without prior warning and for the account of the manufacturer (a representative) of the seized materials.

- Raw material used to manufacture the product - virgin material, primary certified by independent institution

- Production technology - extrusion method.

- Type of connection - socket and sealing ring.

- Socket made from the same material as the pipe; an integral part of each pipe. It guarantees water tightness and strength of the connection.

- Sealing ring - injection molded from EPDM.

- Pipe material: polypropylene PP

- Bright color of the inner layer – easy for video inspection. Color of the outer corrugated layer black or orange-brown (for quantities of at least 900 meters and above).

- Effective pipe length without socket – 3 and 6 m for pipes with sockets and 8 and 12 m for pipes without sockets.

- Roughness of the inner layer <= 0.015 mm.

- Nominal ring stiffness SN ≥ 8 kN/m2, proven by a test protocol.

- Ring flexibility ≥30%, proven by a test protocol.

- Water tightness of the connections - proven by a test protocol, tested at 0.5 bar positive pressure and at -0.3 bar negative pressure (vacuum).

- Nominal diameter ID (inside diameter) for diameters ID1200, ID1400.

- Readable and resistible marking, according the Standard EN13476-3

- Complete system of PP pipes, PP manholes and PP fittings.

- Software for hydraulic (ATV110) and static (ATV127) calculations of the sewage pipes.

- Standard - EN13476, part 1 and part 3.

- Technical specification: