INFRASTRUCTURE SEWERAGE SYSTEM OF POLYPROPYLENE PIPES AND FITTINGS

- Product Description - two-layer polypropylene pipe with a smooth inner layer and a trapezoidal profile for the outer layer - type B, according to BDS EN 13476-3:2018+A1:2020;

- Standard EN 13476-3:2018+A1:2020;

- Raw material for product manufacturing – primary and certified by an independent authority;

- Manufacturing technology – extrusion method;

- Connection method – mechanical - coupling and sealing ring;

- Coupling made from the same material as the pipe, an integral part of the pipe, ensuring watertightness and strength of the connection;

- Possibility to lock the coupled connection to prevent pull-out in unfavorable soil conditions (loess, landslides, swelling soils, etc.) for diameters OD160, OD200, OD250, OD315, OD400;

- Seal: matrix cast from EPDM;

- Pipe material: polypropylene PP-B;

- Inner layer color - light for easy video inspection;

- Outer layer color - different from black;

- Nominal ring stiffness ≥ 16kN/m2, test protocol for each batch;

- Ring flexibility ≥ 30%, test protocol for each batch;

- Watertightness of connections under positive pressure 0.5 bar and under vacuum -0.3 bar, test protocol from an independent laboratory;

- Nominal outer diameter - OD for diameters OD160, OD200, OD250, OD315, and OD400;

- Nominal inner diameter - ID for diameters ID300, ID400, ID500, ID600, ID800, and ID1000;

- Readable and durable marking according to EN 13476-3:2018+A1:2020;

- Complete system of pipes, fittings, and inspection chambers made of PP;

- Compatibility with smooth-walled pipes up to DN/OD400 with guaranteed watertightness;

- Technical specification: